Hot air generator

GVE-GHE-GVEX-GHEX

GVE VERTICAL INDOOR HOT AIR GENERATOR     	GHE HORIZONTAL INDOOR HOT AIR GENERATOR

GVEX VERTICAL OUTDOOR HOT AIR GENERATOR 	GHEX HORIZONTAL OUTDOOR HOT AIR GENERATOR

Sommaire

1.	Introduction	4

1.1.	General	5

1.1.1.	Manufacturer’s liability	5

1.1.2.	Installer’s responsability	5

1.1.3.	User’s liability	5

1.2.	Certifications	6

2.	2. Safety instructions and recommendations	6

2.1.	Safety instructions	6

2.2.	Recommendations	7

3.	Description	8

3.1.	Hot air generator connected to an air duct	8

3.2.	Main parts	9

3.2.1.	Description of Hot air generators -  80 to 200 type	10

3.2.2.	Description of Hot air generator - 250 to 900 type	11

3.3.	Description of operation	12

3.3.1.	Ventilation mode	12

3.3.2.	Heating mode	12

3.3.3.	Stop mode	12

3.3.4.	THERMOSTATS	13

3.3.4.1.	FAN Thermostat	13

3.3.4.2.	LIMIT Thermostat	14

3.3.4.3.	LIMIT2 Thermostat	14

4.	Technical datas	16

5.	DIMENSIONS	17

5.1.	GVE Hot air generators – Vertical indoor models	17

5.2.	GVE Hot air generators – Horizontal indoor models	18

5.3.	GVEX Hot air generators – Vertical outdoor models	19

5.4.	GHEX Hot air generators – Horizontal outdoor models	20

5.5.	Assembling of hot air generator - 600 to 900 models	21

5.5.1.	Assembly of the ventilation section and the heating section.	21

5.5.2.	Assembly of the head (3 paths) to the unit	22

5.5.3.	Assembly of the burner box - GVEX 600 to 900 models	22

5.6.	Accessories	23

5.6.1.	Head (in option)	23

5.6.2.	Filter casing (in option)	24

6.	Installation of the appliance	25

6.1.	General rules	25

6.2.	Location	27

6.2.1.	Loading-Unloading	27

6.2.2.	Connecting air device	27

6.3.	Burner selection	28

6.3.1.	Installation of the burner	28

6.4.	Connecting flue systems	29

6.5.	Evacuation des condensats (Stainless steel heat exchanger)	29

6.6.	Gas connection	30

6.6.1.	General	30

6.6.2.	Accessories	31

7.	Electrical connection	32

7.1.	Connection	32

7.2.	Wiring diagrams	33

7.2.1.	Electrical wiring - From 80 to 200 type	34

7.2.2.	Electrical wiring – From  250 to 500 type	35

7.2.3.	Electrical wiring – From 600 to 750 type	36

7.2.4.	Electrical wiring – 900 type	37

8.	Commissionning	38

8.1.	Start-up	38

9.	Troubleshooting	40

9.1.	Troubleshooting	40

9.2.	Spare parts	44

10.	Maintenance	45

Warranty	48

Introduction

In this manual, the warnings are used to point to specific information. We want to ensure the user safety, to avoid any problem and to ensure proper operation of the appliance.....

WARNING

Indicates a potential hazard which can cause bodily injuries and/or material damage

Indicates important information.

Indicates a reference to other notices or other pages of the manual.

Before installation and commissioning of the device, read carefully all enclosed notices.

Power on

Heating

Ventilation only

Release of the thermal protection of the fan

Release of the LIMIT safety thermostat – manual resetting

Burner off

General

Manufacturer’s liability

Our products are manufactured in compliance with various applicable European directives requirements. They are thus supplied with EC markings and all necessary documents. With our commitment to quality products, we constantly seek to improve them. We therefore reserve the right at any time to modify the characteristics stated in this document.

Our liability as a manufacturer does not apply in the following cases:

- Failure to follow operating instructions for the appliance.

- Failure to maintain or insufficiently maintain of the appliance.

- Failure to follow installation instructions for the appliance.

Installer’s responsability

The installer is responsible for installation and first commissioning of the device. The installer must observe the following:

- Read and follow the instructions given in the instruction manuals provided with the device.

- Carry out installation in accordance with the legislation and standards in force

- Carry out the first commissioning and carry out all necessary controls.

- Explain the installation to the user.

- Inform the user that he cannot make changes in the appliance’s design and to the installation by himself. The slightest modification (change, removal...) of security components or parts automatically results in the appliance’s CE marking becoming invalid.

- Alert the user about the obligation to control and maintain the device.

- Hand all documents to the user

User’s liability

To ensure correct operation of the appliance, the user must observe the following:

- Read and follow the instructions given in the instructions manuals provided with the device.

- Call in a qualified technician to carry out the installation and perform the initial commissioning

- Obtain explanations about the installation by Installer

- Carry out checks and required maintenance.

- Keep all documents in good condition and near the appliance

Certifications

| Appliance | Hot air generator |
| --- | --- |
| Directive | 2009/142/CEE « Gas appliances » |
| Guide line | II2Er3+ |
| Chimney connection | B22 |

2.	Safety instructions and recommendations

Safety instructions

WARNING

The hot air generator is a live device and must be grounded during installation

- It is not allowed to obstruct and/or reduce the space reserved for the room or the appliance vents

- Do not obstruct smoke exhaust or fresh air suction ducts,

- Do not make any change in the settings made by the qualified technician

- Do not place or hang anything on the device,

- Any work on the appliance is prohibited before it is unplugging it from the mains and switching off the gas supply.

- Do not change the used gas type, settings of the appliances, security systems or control settings, as this could lead to dangerous situations.

If the appliance do not operates for a long period, disconnect the power supply of the appliance. When commissioning, it is advisable to use the service of a professional technician. Generally, all repair or maintenance works must be carried out exclusively by authorized and qualified personal.

Subscribing to a maintenance agreement is strongly recommended

Recommendations

The GVE/GHE/GVEX/GHEX Hot air generators are dedicated to the heating of industrial and tertiary premises

The highest attention will thus have to be brought during their installation and during their setting-up.

We recommend to entrust their commissioning to Solaronics Chauffage.

The maintenance of the devices must be made every year, so as to guarantee their availability, to maintain their high performance level and also their safety of functioning.

WARNING

Only qualified professionals are authorized to modify and install the appliance.

- This information forms an integral part of the appliance and must always be kept always with the appliance, even in the event of transfer to another owner or user

- Do not remove or cover the labels and material safety data plates fixed to the devices. Labels and material safety data plates must be readable throughout the device life.

- Install the device in a sufficiently ventilated room,

- Please contact us for any other application other than those described in this document

DON’Ts:

- Do not install hot air generators:

  - In environments with explosive risks,

  - Premises containing vapours of chlorinated products

  - In extremely wet premises (electrical shock hazard)..

Description

The warm air heater is suitable for the following uses:

- Heating of the air, conveyed by its fan unit through the external walls of its combustion chamber and heat exchanger

- Ventilation only

To be used in heating mode, the appliance must be connected to the mains, to a gas network and to a well suited system of evacuation of the products of combustion and condensation.

To be used in ventilation mode, just connect it to the mains.

This warm air heater is to be used to heat the environment air.

The device must not be used for other purposes and in particular for an average outlet air temperature over 80°C, during normal operation.

Hot air generator connected to an air duct

The hot air generator is a device designed to the heating of the industrial or tertiary premises. The hot air distribution can be made by direct blowing or by a duct network.

The system of air distribution represents the terminal and visible part of a heating system. The air distribution conditions the success or not of the installation because it influences the perception of the occupant on its comfort and its sensation of warmth.

IMPORTANT

It is up to the project management to make the sizing of the network of ducts for air recycling and air distribution including accessories (dampers, attenuators, filters), to calculate exactly the static pressure which must be delivered by the device and to specify it at order, to Solaronics Chauffage.

Solaronics Chauffage proposes a wide range of available static pressures, up to 800 Pa, at the exit of devices.

If the pressure delivered by the generator is lower than the need for the installation, the air flow will be lower than its rated value. This will cause or an overheating of the installation or a high number of on/off cycles, and a discomfort. On the contrary if the pressure delivered by the generator is superior to the need for the installation, the air flow will be higher to its rated value, what will cause an overheating of the motor of the ventilator, and also a discomfort

Main parts

The hot air generator can be delivered with Cunod burner

The burner is delivered. It shall be electrically connected to the unit and to the thermostat. Do settings and trials.

Description of Hot air generators -  80 to 200 type

| REP | Designation |  | REP | Designation |
| --- | --- | --- | --- | --- |
| 1 | Air outlet |  | 11 | Combustion chamber |
| 2 | Trapdoor of the smoke box |  | 12 | Fan motor |
| 3 | Flame peephole |  | 13 | Thermostat - Fan-Limit-Limit2 |
| 4 | Anchor plaque burner |  | 14 | Electrical control panel |
| 5 | Centrifugal fan |  | 15 | Air baffles |
| 6 | Recycling air grid (inlet) |  | 16 | Frame in aluminium profiles |
| 7 | Smoke box (front) |  | 17 | Insulated sandwich panels |
| 8 | Flue exhaust |  | 18 | Tensioning device – Engine slider |
| 9 | Smoke box (back) |  | 19 | Pulleys and driving belts |
| 10 | Heat exchanger |  | 20 (*) | Cabinet protection for the burner and electrical components |

(*) GVEX/GHEX type only

GHE / GHEX  models are delivered with bearing feet.

Description of Hot air generator - 250 to 900 type

| REP | Designation |  | REP | Designation |
| --- | --- | --- | --- | --- |
| 1 | Air outlet |  | 11 | Combustion chamber |
| 2 | Trapdoor of the smoke box |  | 12 | Fan motor |
| 3 | Flame peephole |  | 13 | Trithermostat Fan-Limit-Limit2 |
| 4 | Anchor plaque burner |  | 14 | Electrical control panel |
| 5 | Centrifugal fan |  | 15 | Air baffles |
| 6 | Recycling air grid (inlet) |  | 16 | Frame in aluminium profiles |
| 7 | Smoke box (front) |  | 17 | Insulated sandwich panels |
| 8 | Flue exhaust |  | 18 | Tensioning device – Engine slider |
| 9 | Smoke box (back) |  | 19 | Pulleys and driving belts |
| 10 | Heat exchanger |  | 20 (*) | Cabinet protection for the burner and electrical components |

(*)GVEX/GHEX models only

GHE / GHEX  models are delivered with bearing feet.

Description of operation

Ventilation mode

On the electrical panel, the master switch must be placed on the position -1- and the switch on – VENTILATION -. The generator works then permanently as a simple ventilator, whatever is the temperature. The burner does not work.

Heating mode

On the electrical panel, the master switch must be placed on the position -1- and the switch on – HEATING -. As soon as the contact of the regulation of temperature is closed, the burner begins its cycle of auto-diagnosis and pre-sweeping. Then combustion starts. After approximately 2 minutes, when the heat exchanger is enough hot, the thermostat FAN starts automatically fan.

When the contact of the regulation of temperature switches off, the fan continues to work to cool the heat exchanger until the triggering of the FAN thermostat, to avoid blowing cold air.

When the air temperature at the outlet of the generator exceeds the value settled in the thermostat LIMIT (settled in factory at 80°C) the burner stops. Cependant l’unité de ventilation continue à fonctionner pour empêcher que la température de l’air qui sorte du générateur dépasse la limite de sécurité, jusqu’au réenclenchement automatique de ce thermostat

When the air temperature at the outlet of the generator exceeds the value settled in the LIMIT2 thermostat (settled in factory at 100°C), to reset the burner it is necessary to let at first cool the air and then operate as described in the section “TRITHERMOSTAT” of these instructions.

WARNING

The release of LIMIT2 indicates a defect. It is necessary to clear it. In case of impossibility, contact our AFTER SALES SERVICE or a qualified technician

Stop mode

By moving the switch on the position – BURNER STOP -, the burner stops immediately, while fan continues to work until the end of its cooling cycle (FAN thermostat).

To stop definitively all the system, place the master switch on - O-.

WARNING

Before switching off the main switch, check that the hot air generator is enough cooled, not to damage the device.

WARNING

Never switch off the unit from the master switch, but always from the switch or thermostat. In defect the heat stays in the heat exchanger and it risks deforming this one.

THERMOSTATS

A set of 3 thermostats, placed on the heat exchanger, assures the following functions of control and safety:

FAN Thermostat

FAN (TR): thermostat of the ventilation fan, normally opened, to switch on/off automatically the ventilation during HEATING mode.

To set the thermostat FAN remove the lid of the case and adjust the potentiometer by means of a screwdriver. Replace and screw the lid of the case.

The adjustment must be set to 30°C (up to 200 type) and to 25°C (from 250 type).

Higher values delay the starting up of the fan and thus increase the consumption of gas, with the risk of damaging the device. The set temperature of release of the FAN thermostat, for the stop of the fan in phase of cooling, indicated by the first needle to the left, is fixed approximately 14°C lower than the temperature of closure.

It is possible to shunt the FAN thermostat for the applications where a permanent blowing is required (for example the networks of textile ducts): See « Description of the wiring of the tri-thermostats » section

LIMIT Thermostat

LIMIT (TW): maximum temperature of the thermostat of the burner, normally closed, with automatic reset: it adjusts automatically the heating capacity of burner at the minimum, to avoid that the air temperature blown by the generator exceeds the limit of safety. Its setting is fixed at 70°C. This value can be increase up to 80°C maximum, if needed. The ventilation fan is not stopped by the LIMIT thermostat, to cool the heat exchanger. After the cooling of the blown air, the LIMIT automatically resets the burner.

LIMIT2 Thermostat

LIMIT2 (STB): safety thermostat of the burner, normally closed, with manual-reset and positive safety: it stops automatically the burner, to avoid that the air temperature blown by the generator exceeds the limit of safety planned by the reference standard. Its setting is fixed at 100°C and must not be modified, not to overheat excessively the generator. The ventilation fan is not stopped by the thermostat LIMIT2, to cool the heat exchanger.

To reset the LIMIT2: wait at first that the air temperature at the outlet cools down, until the stop of the fan, and press on the green button

WARNING

The release of LIMIT2 indicates a defect. It is necessary to clear it. In case of impossibility, contact our AFTER SALES SERVICE or a qualified technician.

3.4.4.4.	Description of the wiring of the tri-thermostats

Standard models

Permanent ventilation

Technical datas

| THERMAL DATA | MOD. | 80 | 100 | 125 | 150 | 175 | 200 | 250 | 300 | 375 | 425 | 500 | 600 | 750 | 900 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| RATED HEAT INPUT Qn | kW | 104,7 | 128,6 | 164,5 | 192,1 | 223,1 | 257,8 | 318,7 | 387,2 | 482,3 | 541,9 | 632,3 | 763,4 | 957,3 | 1136,3 |
| RATED HEATING CAPACITY Pn | kW | 95,3 | 116,3 | 148,9 | 173,3 | 203,5 | 232,6 | 290,7 | 348,8 | 436,0 | 494,2 | 569,8 | 697,7 | 872,1 | 1046,5 |
| THERMAL EFFICIENCY At rated heating capacity Pn | % | 91,2 | 90,4 | 90,5 | 90,2 | 91,2 | 90,2 | 91,2 | 90,1 | 90,4 | 91,2 | 90,1 | 91,4 | 91,3 | 92,1 |
| BACK PRESSURE IN THE COMBUSTION CHAMBER | mbar | 0,23 | 0,25 | 0,2 | 0,25 | 0,3 | 0,35 | 0,5 | 0,7 | 0,7 | 0,9 | 1 | 0,9 | 0,9 | 1,2 |
| VOLUME OF THE COMBUSTION CHAMBER | m³ | 0,24 | 0,24 | 0,33 | 0,33 | 0,76 | 0,76 | 0,95 | 0,95 | 1,44 | 1,7 | 1,7 | 2,7 | 3,27 | 4,44 |
| VOLUME OF THE COMBUSTION CIRCUIT | m³ | 0,32 | 0,32 | 0,46 | 0,46 | 0,98 | 0,98 | 1,2 | 1,2 | 1,72 | 2,2 | 2,2 | 3,46 | 4,19 | 5,55 |
| MIN. AIR VOLUME MIN. FOR PRESWEEPING | m³ (1) | 1,6 | 1,6 | 2,3 | 2,3 | 5 | 5 | 6 | 6 | 8,6 | 11 | 11 | 17,3 | 20,95 | 27,76 |
| GAS CATEGORY | FRANCE | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ | II2Er3+ |
| AERAULIC DATA |
| AIR FLOW RATE | m³/h à 18° | 6.300 | 7.800 | 9.700 | 11.700 | 13.700 | 15.600 | 19.800 | 23.500 | 29.200 | 33000 | 38700 | 46500 | 55200 | 69500 |
| AVAILABLE STATIC PRESSURE | Pa (2) | 170 | 150 | 200 | 220 | 210 | 190 | 170 | 200 | 190 | 220 | 160 | 240 | 260 | 290 |
| Average temperature of by-products with an air comburant temperature of 20°C | °C | 196 | 228 | 229 | 241 | 202 | 230 | 211 | 234 | 221 | 202 | 234 | 190 | 195 | 182 |
| GAS FLOW RATE at 0°c – 1013 mbar |
| G20 - 20mbar | m³/h | 11,10 | 13,60 | 17,40 | 20,30 | 23,60 | 27,30 | 33,80 | 41,00 | 51,10 | 57,40 | 67,00 | 80,80 | 101,40 | 120,30 |
| G25 - 25mbar | m³/h | 12,80 | 15,80 | 20,20 | 23,60 | 27,40 | 31,70 | 39,20 | 47,60 | 59,30 | 66,70 | 77,80 | 94,00 | 117,80 | 140,00 |
| G31 - 37mbar | kg/h | 7,97 | 9,80 | 12,53 | 14,63 | 17,00 | 19,64 | 24,28 | 29,50 | 36,74 | 41,28 | 48,17 | 58,15 | 72,92 | 86,55 |
| FUEL - PCI 10.200Kcal/kg | kg/h | 8,8 | 10,8 | 13,9 | 16,2 | 18,8 | 21,7 | 26,9 | 32,6 | 40,7 | 45,7 | 53,3 | 64,4 | 80,7 | 95,8 |
| ELECTRICAL DATA FOR A STANDARD UNIT |
| FAN MOTOR Electrical capacity | kW x n° | 1,1 | 1,5 | 1,5 | 2,2 | 2,2 | 3 | 2,2x2 | 3x2 | 3x2 | 4x2 | 5,5x2 | 4x3 | 5,5x3 | 5,5x4 |
| FAN MOTOR CURRENT (400V 3F) | A | 2,9 | 3,6 | 3,6 | 5,1 | 5,1 | 7 | 5,1x2 | 7x2 | 7x2 | 9,2x2 | 12x2 | 9,2x3 | 12x3 | 12x4 |
| FAN MOTOR CURRENT ( 230V 3F) | A | 4,8 | 6,2 | 6,2 | 9,3 | 9,3 | 12 | 9,3x2 | 12x2 | 12x2 | 15x2 | 20x2 | 15x3 | 20x3 | 20x4 |
| NIVEAU SONORE (à 4 m de distance) | dB(A) | 71 | 72 | 73 | 72 | 72 | 73 | 74 | 75 | 75 | 75 | 76 | 75 | 76 | 78 |
| ELECTRICAL DATA FOR A UNIT WITH AN AVAILABLE STATIC PRESSURE OF 300 Pa |
| FAN MOTOR Electrical capacity | kW x n° | 1,5 | 2,2 | 2,2 | 3 | 3 | 4 | 2 x 3 | 2 x 4 | 2 x 4 | 2 x 5,5 | 2 x 7,5 | 3 x 5,5 | / | / |
| FAN MOTOR CURRENT (400V 3F) | A | 3.45 | 4,9 | 4,9 | 6,47 | 6,47 | 8,36 | 2 x 6,47 | 2 x 8,26 | 2 x 8,26 | 2 x 11,1 | 2 x 14,6 | 3 x 11,1 | / | / |
| 1) According EN1020 Standards 2) Hot air generator without air inlet filters. Pressure drops of filters indicated page ¨FILTER CASING¨ |

DIMENSIONS

GVE Hot air generators – Vertical indoor models

Connection of the head

HEAD

Connection of an air duct

Connection of a recycling air duct

FILTRE

In standard configuration the recycling air grid is to the left of the burner until the model 200, and to the right from the model 250.

This position can be reversed on request (see drawing: recycling air grid to the right of the burner)

| VERTICAL HOT AIR GENERATOR | Head Height | Smoke connection Height | Air outlet connection | Air inlet connection | Fame profile | Chimney | Weight of generator | Weight of head |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Length | Width | Height |  |  |  |  |  |  | net | gross |  |
| Type | A | B | C | D | E | F | G | H | I | L |  | kg | kg | kg |
| GVE 80 | 1000 | 750 | 1900 | 405 | 1675 | 670 | 920 | 770 | 920 | 40 | 200 | 315 | 325 | 27 |
| GVE 100 | 1000 | 750 | 1900 | 405 | 1675 | 670 | 920 | 770 | 920 | 40 | 200 | 325 | 335 | 27 |
| GVE 125 | 1260 | 900 | 2060 | 405 | 1750 | 820 | 1180 | 760 | 1180 | 40 | 250 | 480 | 493 | 35 |
| GVE 150 | 1260 | 900 | 2060 | 405 | 1750 | 820 | 1180 | 760 | 1180 | 40 | 250 | 490 | 503 | 35 |
| GVE 175 | 1440 | 1020 | 2340 | 405 | 1975 | 940 | 1360 | 760 | 1360 | 40 | 250 | 555 | 570 | 42 |
| GVE 200 | 1440 | 1020 | 2340 | 405 | 1975 | 940 | 1360 | 760 | 1360 | 40 | 250 | 580 | 595 | 42 |
| GVE 250 | 1790 | 1020 | 2340 | 405 | 1975 | 940 | 1710 | 760 | 1710 | 40 | 300 | 820 | 840 | 50 |
| GVE 300 | 1790 | 1020 | 2340 | 405 | 1975 | 940 | 1710 | 760 | 1710 | 40 | 300 | 850 | 870 | 50 |
| GVE 375 | 1960 | 1280 | 2660 | 405 | 2280 | 1200 | 1880 | 930 | 1880 | 40 | 300 | 1200 | 1230 | 62 |
| GVE 425 | 2300 | 1340 | 2660 | 405 | 2280 | 1260 | 2220 | 930 | 2220 | 40 | 300 | 1480 | 1515 | 78 |
| GVE 500 | 2300 | 1340 | 2660 | 405 | 2280 | 1260 | 2220 | 930 | 2220 | 40 | 300 | 1550 | 1585 | 78 |
| GVE 600 | 2820 | 1550 | 2960 | 445 | 2572 | 1470 | 2740 | 970 | 2740 | 40 | 350 | 1850 | 1935 | 100 |
| GVE 750 | 2820 | 1620 | 3100 | 445 | 2672 | 1540 | 2740 | 970 | 2740 | 40 | 400 | 2300 | 2395 | 120 |
| GVE 900 | 3720 | 1620 | 3100 | 445 | 2672 | 1540 | 3640 | 970 | 3640 | 40 | 400 | 2800 | 2920 | 153 |

REMARK: GVE 600, GVE 750 and GVE 900 models are built in 2 sections with the height of

C1 and C2 corresponding to the section of ventilation and heating one’s as follows:

GVE 600 Model C1=1050 mm C2=1910 mm

GVE 750 Model C1=1050 mm C2=2050 mm

GVE 900 Model C1=1050 mm C2=2050 mm

GVE Hot air generators – Horizontal indoor models

Connection of a head

Connection fo an air duct

The head is the same as for « GVE » models.

AIR INLET GRID: on request position 1 - 2 – 3.

The order must indicate the positioning (right or left)

The drawing shows the left positioning (blowing direction).

Connection of a recycling air duct

| HORIZONTAL INDOOR HOT AIR GENERATOR | Head Height | Smoke connection Height | Air outlet connection | Air inlet connection | Fame profile | Chimney | Weight of generator | Weight of head |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Length | Height | Width |  |  |  |  |  |  | net | Gross |  |
| MOD. | A | B | C | D | E | F | G | H | I | L |  | kg | kg | kg |
| GHE 80 | 1000 | 850 | 2200 | 405 | 1975 | 770 | 920 | 1070 | 920 | 40 | 200 | 320 | 330 | 27 |
| GHE 100 | 1000 | 850 | 2200 | 405 | 1975 | 770 | 920 | 1070 | 920 | 40 | 200 | 338 | 348 | 27 |
| GHE 125 | 1260 | 900 | 2060 | 405 | 1750 | 820 | 1180 | 760 | 1180 | 40 | 250 | 485 | 498 | 35 |
| GHE 150 | 1260 | 1020 | 2060 | 405 | 1750 | 940 | 1180 | 760 | 1180 | 40 | 250 | 504 | 517 | 39 |
| GHE 175 | 1440 | 1020 | 2340 | 405 | 1975 | 940 | 1360 | 760 | 1360 | 40 | 250 | 560 | 575 | 42 |
| GHE 200 | 1440 | 1020 | 2340 | 405 | 1975 | 940 | 1360 | 760 | 1360 | 40 | 250 | 585 | 600 | 42 |
| GHE 250 | 1790 | 1020 | 2600 | 405 | 2235 | 940 | 1710 | 1020 | 1710 | 40 | 300 | 837 | 857 | 50 |
| GHE 300 | 1790 | 1020 | 2600 | 405 | 2235 | 940 | 1710 | 1020 | 1710 | 40 | 300 | 867 | 887 | 50 |
| GHE 375 | 1960 | 1280 | 2960 | 405 | 2580 | 1200 | 1880 | 1230 | 1880 | 40 | 300 | 1225 | 1255 | 62 |
| GHE 425 | 2300 | 1340 | 2960 | 405 | 2580 | 1260 | 2220 | 1230 | 2220 | 40 | 300 | 1508 | 1543 | 78 |
| GHE 500 | 2300 | 1340 | 2960 | 405 | 2580 | 1260 | 2220 | 1230 | 2220 | 40 | 300 | 1578 | 1613 | 78 |
| GHE 600 | 2820 | 1550 | 3260 | 445 | 2872 | 1470 | 2740 | 1270 | 2740 | 40 | 350 | 1890 | 1980 | 100 |
| GHE 750 | 2820 | 1620 | 3400 | 445 | 2972 | 1540 | 2740 | 1270 | 2740 | 40 | 400 | 2340 | 2440 | 120 |
| GHE 900 | 3720 | 1620 | 3400 | 445 | 2972 | 1540 | 3640 | 1270 | 3640 | 40 | 400 | 2845 | 2975 | 153 |

REMARK: GHE 600, GHE 750 and GHE 900 models are built in 2 sections with the height of

C1 and C2 corresponding to the section of ventilation and heating one’s as follows:

GHE 600 Model C1=1050 mm C2=1910 mm

GHE 750 Model C1=1050 mm C2=2050 mm

GHE 900 Model C1=1050 mm C2=2050 mm

GVEX Hot air generators – Vertical outdoor models

Connection of an air duct

Connection of a recycling air duct

In standard configuration the recycling air grid is to the left of the burner until the model 200, and to the right from the model 250.

This position can be reversed on request (see drawing: recycling air grid to the right of the burner)

| VERTICAL OUTDOOR HOT AIR GENERATOR | Smoke connection Height | Air outlet connection | Air inlet connection | Burner section | Chimney | Weight of generator |
| --- | --- | --- | --- | --- | --- | --- |
|  | Length | Height | Width |  |  |  | Depth | Width |  | Net | Gross |
| MOD. | A | B | C | E | F | G | H | I | N | O |  | kg | kg |
| GVEX 80 | 1000 | 750 | 1900 | 1675 | 670 | 920 | 770 | 920 | 700 | 1580 | 200 | 357 | 367 |
| GVEX 100 | 1000 | 750 | 1900 | 1675 | 670 | 920 | 770 | 920 | 700 | 1580 | 200 | 367 | 377 |
| GVEX 125 | 1260 | 900 | 2060 | 1750 | 820 | 1180 | 760 | 1180 | 700 | 1780 | 250 | 527 | 540 |
| GVEX 150 | 1260 | 900 | 2060 | 1750 | 820 | 1180 | 760 | 1180 | 700 | 1780 | 250 | 537 | 550 |
| GVEX 175 | 1440 | 1020 | 2340 | 1975 | 940 | 1360 | 760 | 1360 | 700 | 2130 | 250 | 615 | 630 |
| GVEX 200 | 1440 | 1020 | 2340 | 1975 | 940 | 1360 | 760 | 1360 | 700 | 2130 | 250 | 640 | 655 |
| GVEX 250 | 1790 | 1020 | 2340 | 1975 | 940 | 1710 | 760 | 1710 | 700 | 2130 | 300 | 880 | 900 |
| GVEX 300 | 1790 | 1020 | 2340 | 1975 | 940 | 1710 | 760 | 1710 | 800 | 2130 | 300 | 910 | 930 |
| GVEX 375 | 1960 | 1280 | 2660 | 2280 | 1200 | 1880 | 930 | 1880 | 1000 | 2345 | 300 | 1271 | 1301 |
| GVEX 425 | 2300 | 1340 | 2660 | 2280 | 1260 | 2220 | 930 | 2220 | 1000 | 2410 | 300 | 1556 | 1591 |
| GVEX 500 | 2300 | 1340 | 2660 | 2280 | 1260 | 2220 | 930 | 2220 | 1000 | 2410 | 300 | 1626 | 1661 |
| GVEX 600 | 2820 | 1550 | 2960 | 2572 | 1470 | 2740 | 970 | 2740 | 1200 | 2710 | 350 | 1944 | 2014 |
| GVEX 750 | 2820 | 1620 | 3100 | 2672 | 1540 | 2740 | 970 | 2740 | 1200 | 2850 | 400 | 2426 | 2511 |
| GVEX 900 | 3720 | 1620 | 3100 | 2672 | 1540 | 3640 | 970 | 3640 | 1200 | 2850 | 400 | 2926 | 3035 |

REMARK: GVEX 600, GVEX 750 and GVEX 900 models are built in 2 sections with the height of

C1 and C2 corresponding to the section of ventilation and heating one’s as follows:

GVEX 600 Model C1=1050 mm C2=1910 mm

GVEX 750 Model C1=1050 mm C2=2050 mm

GVEX 900 Model C1=1050 mm C2=2050 mm

GHEX Hot air generators – Horizontal outdoor models

Connection of an air duct

Connection of a recycling air duct

The head is the same as for « GVE » models.

AIR INLET GRILL: on request position 1 - 2 – 3.

The order must indicate the positioning (right or left)

The drawing shows the left positioning (blowing direction).

| HORIZONTAL OUTDOOR HOT AIR GENERATOR | Smoke connection Height | Air outlet connection | Air inlet connection | Burner section | Chimney | Weight of generator |
| --- | --- | --- | --- | --- | --- | --- |
|  | Length | Height | Width |  |  |  | Depth | Width |  | Net | Gross |
| MOD. | A | B | C | E | F | G | H | I | N | O |  | kg | kg |
| GHEX 80 | 1000 | 850 | 2200 | 1975 | 770 | 920 | 1070 | 920 | 700 | 2100 | 200 | 357 | 367 |
| GHEX 100 | 1000 | 850 | 2200 | 1975 | 770 | 920 | 1070 | 920 | 700 | 2200 | 200 | 367 | 377 |
| GHEX 125 | 1260 | 900 | 2060 | 1750 | 820 | 1180 | 760 | 1180 | 700 | 2060 | 250 | 527 | 540 |
| GHEX 150 | 1260 | 1020 | 2060 | 1750 | 940 | 1180 | 760 | 1180 | 700 | 2060 | 250 | 545 | 557 |
| GHEX 175 | 1440 | 1020 | 2340 | 1975 | 940 | 1360 | 760 | 1360 | 700 | 2340 | 250 | 615 | 630 |
| GHEX 200 | 1440 | 1020 | 2340 | 1975 | 940 | 1360 | 760 | 1360 | 700 | 2340 | 250 | 640 | 655 |
| GHEX 250 | 1790 | 1020 | 2600 | 2235 | 940 | 1710 | 1020 | 1710 | 700 | 2600 | 300 | 897 | 917 |
| GHEX 300 | 1790 | 1020 | 2600 | 2235 | 940 | 1710 | 1020 | 1710 | 800 | 2600 | 300 | 927 | 937 |
| GHEX 375 | 1960 | 1280 | 2960 | 2580 | 1200 | 1880 | 1230 | 1880 | 1000 | 2960 | 300 | 1296 | 1329 |
| GHEX 425 | 2300 | 1340 | 2960 | 2580 | 1260 | 2220 | 1230 | 2220 | 1000 | 2960 | 300 | 1584 | 1619 |
| GHEX 500 | 2300 | 1340 | 2960 | 2580 | 1260 | 2220 | 1230 | 2220 | 1000 | 2960 | 300 | 1654 | 1689 |
| GHEX 600 | 2820 | 1550 | 3260 | 2872 | 1470 | 2740 | 1270 | 2740 | 1200 | 3260 | 350 | 1978 | 2048 |
| GHEX 750 | 2820 | 1620 | 3400 | 2972 | 1540 | 2740 | 1270 | 2740 | 1200 | 3400 | 400 | 2461 | 2546 |
| GHEX 900 | 3720 | 1620 | 3400 | 2897 | 1540 | 3640 | 1270 | 3640 | 1200 | 3400 | 400 | 2968 | 3077 |

REMARK: GHEX 600, GHEX 750 and GHEX 900 models are built in 2 sections with the height of

C1 and C2 corresponding to the section of ventilation and heating one’s as follows:

GHEX 600 Model C1=1050 mm C2=1910 mm

GHEX 750 Model C1=1050 mm C2=2050 mm

GHEX 900 Model C1=1050 mm C2=2050 mm

Assembling of hot air generator - 600 to 900 models

For reasons of size and weight, hot air generators - 600 to 900 models -

are delivered in 2 sections (ventilation section and heating section).

Assembly of the ventilation section and the heating section.

For this operation a bag with screws and joints is delivered with the device

1. Unpack the 2 sections

2. Position the ventilation section on a flat floor

3. Put the gasket (2) self, staffing, along the side of the aluminium profiles that must be hit with that of the heater

4. Put the heating section on the ventilation one’s, by lifting it by the rings on the heat exchanger

5. For GHE and GHEX models, assembly horizontally the 2 sections

6. Fix the sections with screws on the flanges (1) of the ventilation section

7. Connect the thermostat to the electrical box with the supplied electrical cable

Assembly of the head (3 paths) to the unit

► Unpack the head

► Put the head on the heating section

► Screw the plenum on the flanges (1) of the section of heater

► Fix the head on the generator with 4 legs staffing, screw on the corners of the lengthy coastline. Make holes on site.

Assembly of the head (3 paths)

Assembly of the burner box - GVEX 600 to 900 models

►  Press the edge (4) of the cabin on the burner higher profile generator, side burner.

►  Drill on the lateral profiles matching flanges 4 (3) of the cabin (hole Ø 5 mm);

►  Tighten the clamps with the screws Staffing

Assembly of the burner box

Accessories

Head (in option)

The air is blown through grids located on 3 faces of the head

| TYPE | P (mm) | Q (mm) | D (mm) | R (mm) | T (mm) | S (mm) | Number of grids 1) | Air throw (m) 2) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  | max | min |  |
| GVE 80 | 915 | 665 | 405 | 550 | 550 | 300 | 1+1+1 | 34 | 34 |  |
| GVE 100 | 915 | 665 | 405 | 550 | 550 | 300 | 1+1+1 | 38 | 38 |  |
| GVE 125 | 1175 | 815 | 405 | 650 | 650 | 300 | 1+1+1 | 40 | 40 |  |
| GVE 150 | 1175 | 815 | 405 | 650 | 650 | 300 | 1+1+1 | 46 | 46 |  |
| GVE 175 | 1355 | 935 | 405 | 750 | 750 | 300 | 1+1+1 | 55 | 55 |  |
| GVE 200 | 1355 | 935 | 405 | 750 | 750 | 300 | 1+1+1 | 60 | 60 |  |
| GVE 250 | 1705 | 935 | 405 | 750 | 750 | 300 | 1+2+1 | 74 | 60 |  |
| GVE 300 | 1705 | 935 | 405 | 750 | 750 | 300 | 1+2+1 | 80 | 62 |  |
| GVE 375 | 1875 | 1195 | 405 | 750 | 750 | 300 | 1+2+1 | 80 | 63 |  |
| GVE 425 | 2215 | 1255 | 405 | 650 | 750 | 300 | 1+3+1 | 90 | 69 |  |
| GVE 500 | 2215 | 1255 | 405 | 650 | 750 | 300 | 1+3+1 | 94 | 72 |  |
| GVE 600 | 2735 | 1465 | 445 | 750 | 550 | 300 | 2+3+2 | 102 | 84 |  |
| GVE 750 | 2735 | 1535 | 445 | 750 | 650 | 300 | 2+3+2 | 108 | 89 |  |
| GVE 900 | 3635 | 1535 | 445 | 750 | 650 | 300 | 2+4+2 | 118 | 95 |  |
| Short side (Q) + long side (P) + Short side (Q) The air throw is given for a final speed of the air of 0.15 m /sec., provided that the fins of the grids are not tilted. For a tilt of 30 °, multiply the value of the air throw, indicated in the above tab, by 0.65 |

Filter casing (in option)

| TYPE | U (mm) | V (mm) | Z (mm) | Y (mm) | X (mm) | Dimensions of filters (1) | Pressure drop [Pa] (2) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GVE 80 | 980 | 780 | 60 | 890 | 735 | 1x780x900x48 | 30 |
| GVE 100 | 980 | 780 | 60 | 890 | 735 | 1x780x900x48 | 45 |
| GVE 125 | 1260 | 840 | 200 | 1220 | 800 | 2x625x400x98 2x500x400x98 | 45 |
| GVE 150 | 1260 | 840 | 200 | 1220 | 800 | 2x625x400x98 2x500x400x98 | 50 |
| GVE 175 | 1440 | 840 | 200 | 1400 | 800 | 4x625x400x98 | 50 |
| GVE 200 | 1440 | 840 | 200 | 1400 | 800 | 4x625x400x98 | 60 |
| GVE 250 | 1790 | 840 | 200 | 1750 | 800 | 2x625x400x98 4x500x400x98 | 64 |
| GVE 300 | 1790 | 840 | 200 | 1750 | 800 | 2x625x400x98 4x500x400x98 | 80 |
| GVE 375 | 1960 | 1010 | 300 | 1880 | 930 | 4x500x500x98 4x500x400x98 | 80 |
| GVE 425 | 2300 | 1010 | 300 | 2220 | 930 | 8x500x500x98 | 63 |
| GVE 500 | 2300 | 1010 | 300 | 2220 | 930 | 8x500x500x98 | 75 |
| GVE 600 | 2820 | 1050 | 300 | 2740 | 970 | 2x625x500x98 8x500x500x98 | 75 |
| GVE 750 | 2820 | 1050 | 300 | 2740 | 970 | 2x625x500x98 8x500x500x98 | 100 |
| GVE 900 | 3720 | 1050 | 300 | 3640 | 970 | 8x625x500x98 4x500x500x98 | 100 |
| Efficiency according to ASHRAE52/76 Pressure drops given for a new filter. Caution! For blocked filters, this pressure drop shall be increased by 50%, at least. The pressure drop must be subtracted from the pressure available on the generator |

- Filter casing - GVE 80 to GVE 100 models

- Filter casing - GVE 125 to GVE 900 models

Assembly of the filter casing:

Place a foamed plastic seal.

Place and fix the casing filter on the air inlet thanks to self drilling screws.

Removal of filters:

Undo the upper side screws. Remove the steel cover placed at the top so as to access to filters.

Installation of the appliance

CAUTION

The installation of gas appliances must be made by qualified and authorized personnel. It depends on the characteristics of premises, in volume, in location and in equipment of exhaust ducts or devices of ventilation which these premises have or can be provided

Packaging:

The hot air heater is delivered on a pallet, and is protected by a pluribol film. The air inlet plenum, if installed, is packaged together with heater or separately, according to the models

Reception – Storage

It is essential to check the state of the delivery (even if the packaging is intact) and its conformity with regard to the order.

Proceed to the unpacking of the device by using adequate protection equipments. Check the state of the devices. In case of doubt, do not use it, but contact the manufacturer or its representatives. In case of damage or of missing parts, you have to put the observations on the receipt of the carrier in the most precise possible way, (Remark: the mention "subject to unpacking" has no legal value), then to confirm these reserves by registered letter under 48 hours to the carrier. It is of the responsibility of the buyer to check the delivered goods. No appeal will be possible if this procedure is not respected.

Store the goods in clean and dry premises, shielded from the shocks, the vibrations, the temperature differences and in an atmosphere of hygrometry lower than 90 %.

General rules

Hot air generators can be installed:

- either directly in the premises to be heated

- either in a boiler room/technical room

- or outside

However, this facility is subject to the national security.  If in doubt, check with safety and inspection bodies

Ventilation:

Premises receiving gas appliances should be provided with permanent ventilation in accordance with the rules in force in the country of installation

Gas connection:

Before installing the appliance, it is necessary to check that the local distribution conditions (gas type, pressure) are compatible with settings of the device to be installed

WARNING

Do not turn upside down the generator. It could damage it.

WARNING

Minimum distances required for maintenance and safety devices:

Smoke connection

Hot air gnerator

Burner

| TYPE | A (1) (mm) | B (2) (mm) | C (mm) |
| --- | --- | --- | --- |
| 80 | 1000 | 500 | 300 |
| 100 | 1000 | 500 | 300 |
| 125 | 1300 | 500 | 600 |
| 150 | 1300 | 500 | 600 |
| 175 | 1300 | 570 | 600 |
| 200 | 1300 | 570 | 600 |
| 250 | 1300 | 650 | 600 |
| 300 | 1300 | 650 | 600 |
| 375 | 1500 | 650 | 600 |
| 425 | 1700 | 650 | 600 |
| 500 | 1700 | 650 | 600 |
| 600 | 2000 | 700 | 600 |
| 750 | 2000 | 800 | 600 |
| 900 | 2000 | 800 | 600 |
| (1) This dimention shall be checked according dimensions and type of burner. (2) Check this dimension so as to make possible the dismantling of the smoke connection |

Furthermore it is necessary to leave an appropriate clearance around the generator, free of combustible materials, on a distance calculated according to the prescriptions and existing standards

Location

The generator must be installed according to the prescriptions, the laws, the standards and the regulation in force which the installer has to know.

- Try to sweep with the air jet the whole zone to be warmed.

- In the case of an important infiltration of outside air, compensate it with a hot airflow

- Avoid managing air jets against obstacles such as pillars or stored boxes

- If the premises are equipped with exhaust fans, install the generator on the opposite wall and to install an air inlet to renew the extracted air.

Loading-Unloading

The transport, the loading and the unloading must be made with the greatest care.

During these operations of loading and unloading, the center of gravity of the device has to stay in the center, by avoiding the dangerous slopes.

Raise the device with a power lift truck, or by means of a crane, of a sufficient capacity with taking into account of the safety factor (check the gross weight of the device in the tab and its dimensions).

In any case, be careful not to damage the unit by using suitable protections.

Connecting air device

It is recommended to put sealing devices or joint putty for the connecting of the generator to:

- An air mixing box

- A head

- An air distribution network

Burner selection

Forced-draught gas burner. The installer must select a burner, EC labeled according the Directive 2009/142/CEE « Gas appliances » and compatible with the generator. It shall be set in accordance with the technical data indicated page 15 of these instructions. (§ Technical data).

According the model of generator, the burner must be chosen with a short or long combustion (please read the hereafter tab)

Installation of the burner

CAUTION

For all operations described hereunder, the installer must follow the instructions of the burner manufacturer.

1.  Prepare the burner plate (4) and fix the burner o it, using bolts prescribed in the instructions of the burner

2.  Do the electrical connections from the burner to the generator electrical box, according to our wiring diagrams (§ Electrical wiring) according the generator model.

3. Do electrical connections of the LIMIT and LIMIT2 thermostats, from the burner to the electrical box.

4.  Do the electrical connections of the control box (In option: Communicating control box or air ambient thermostat).

COMBUSTION CHAMBER

BURNER PLATE

BURNER

WARNING:

To maximize the use of the length of the combustion chamber and prevent the flame slapping against the back of the room itself, do install a burner with a combustion head witch  length"A" is between a minimum and a maximum as indicated in the hereby table.

| Type | A min. (mm) | A max. (mm) |
| --- | --- | --- |
| 80 | 190 | 240 |
| 100 | 190 | 240 |
| 125 | 190 | 240 |
| 150 | 190 | 240 |
| 175 | 215 | 290 |
| 200 | 215 | 290 |
| 250 | 215 | 290 |
| 300 | 215 | 290 |
| 375 | 240 | 340 |
| 425 | 240 | 340 |
| 500 | 240 | 340 |
| 600 | 240 | 340 |
| 750 | 265 | 390 |
| 900 | 265 | 390 |

ATTENTION :

Pour exploiter au mieux la longueur de la chambre de combustion et éviter que la flamme tape contre le fond de la chambre même, il faut introduire la tête de combustion du brûleur d’une longueur “A” qui soit entre un minimum et un maximum comme indiqué dans la présente liste

ATTENTION :

Pour exploiter au mieux la longueur de la chambre de combustion et éviter que la flamme tape contre le fond de la chambre même, il faut introduire la tête de combustion du brûleur d’une longueur “A” qui soit entre un minimum et un maximum comme indiqué dans la présente liste

ATTENTION :

Pour exploiter au mieux la longueur de la chambre de combustion et éviter que la flamme tape contre le fond de la chambre même, il faut introduire la tête de combustion du brûleur d’une longueur “A” qui soit entre un minimum et un maximum comme indiqué dans la présente liste

Connecting flue systems

For the correct operation of the heater and environment protection, it must be connected to a suitable sized chimney, built with special materials and in accordance with local, national, and European standards and rules in force.

Prévoir toujours à la base de la cheminée une chambre de récolte cendre et condensât, pour ne pas le faire entrer dans la boite à fumée de l’appareil.

Evacuation of the condensates (Stainless steel heat exchanger)

Pipes of the heat exchanger are tilted so as to make easy the evacuation of the condensates towards the back smoke box. The heating appliance is supplied with a siphon for condensate evacuating. The siphon is delivered separately and has to set at the installation of the appliance.

WARNING

Draining must be carried out with acid water resistant materials.

Do not use copper or galvanized pipes.

- For condensation water flow system, use PVC pipes of diameter at least equal to 20 mm). Make sure that the pipe is always positioned under the siphon top point.

- Check tightness of condensation water evacuation pipes.

- Before using the appliance, fill the siphon with water through the filling cap. This prevents the release of smoke into the water during the commissioning.

Frost protection

The condensate draining, including the siphon must be protected from frost. It is best to keep the draining ducts inside a frost protected premise. If it is outside of the building, the part of the pipe behind the siphon must be open to avoid any eventual ice from closing the spill. Take all necessary measures to prevent such incident, it may cause irreversible damage to the heater.

Neutralisation of condensation water

The acidity of the water generated by the combustion of the natural gas is pH = 3.5 to 3.8. Some regulations on pollutant discharges require treatment of these condensates. In this case, prepare a condensate neutralisation kit (not supplied).

Gas connection

General

Firstly, you should check that the device you have received is consistent with the distributed gas type. To do this, you should refer to the information given on the heater rating plate.

The gas supply must match the heater output and be equipped with all safety and control devices provided by standards.

A detailed study will be carried out on duct diameters depending on the type, flow of gas and the ducts length. It should be checked that ducts pressure drop does not exceed 5% of the supply pressure.

The gas connections must be performed in accordance with indoor installations requirements regardless the type of gas, by qualified personnel having the applicable approvals

Before commissioning, ensure that the gas line is tight and clean all residues caused by the work.

A manual isolation valve must be settled near the generator so as to be able to isolate the burner of gas supply line for the operations of maintenance and repairs

WARNING

Before opening the gas network, check the valve tightness to the appliance heating unit

When the generator is settled outside, check that all the parts of the gas line (shut off valve, filter, reducing valve) are designed for negative temperatures and protect them against the bad weather.

Accessories

According to the pressure, to the heating capacity of the installation, Solaronics Chauffage proposes a range of accessories of line:

- Isolation valve

- Filters

- Reducing valves

(1) Shut off valve - (2) Gas filter - (3) Reducing valve

Examples of gas connection

Electrical connection

Connection

The electric installation must be realized by respecting the standards and the national and local regulations. All the internal electric connections of the generator are made in factory. The connecting of the general supply and of the remote control or the indoor thermostat must be realized by the installer, following electrical drawings; refer to "electrical drawings" section.

- Check the electrical installation:

o 3 x 400V 50Hz + N, non floating neutral (ie 0V between the ground and the neutral)

If necessary a transformer of isolation must be settled.

- Isolate totally the generator from the main electric line, by means of an all-pole switch settled upstream to the generator, according to the standards and adapted to the total electric power of the generator.

- Connect the power supply and the ground to the terminal board located inside the electrical box of the generator.

- If necessary connect the fire dampers to terminal board located inside the electrical box of the generator.

WARNING

Modify on no account the cabling of the LIMIT and LIMIT2 safety thermostats.

WARNING

In case an additional clock settled, do not connect it in series with the power supply but with the indoor thermostat. In defect the release of the clock switches off the generator and the residual heat can damage the device.

Wiring diagrams

Diagrams below are in force in the case of standard generators. When the unit includes options, the wiring diagram is delivered with the unit. In this case keep it carefully.

Electrical boxes of generators of standard types

Electrical wiring - From 80 to 200 type

T2

T1

Electrical wiring – From  250 to 500 type

T1

T2

Electrical wiring – From 600 to 750 type

T1

T2

Electrical wiring – 900 type

T1

T2

Commissionning

Start-up

WARNING

Do not remove guards at the air inlet of the generator.

1- Before commissioning and turning on the generator, check that all connections have been carried out as defined above:

- « Exhaust ducts connection» section

- « Condensate connection» section (stainless steel heat exchanger)

- « Gas connection» section

- « Electrical connection» section

- « Air connection» section

Check also:

- That an appropriate clearance around the generator has been left

- That nothing blocks the air inlets and outlets. If a head is set, check that louvers are opened. If there is a filter, check that it is clean.

- That all electrical connections have been carried out

- That the connection to the ground is effective

- That the FAN, LIMIT and LIMIT2 thermostats are set to the right values

- That the position of the bulbs-sensors of the Thermostat is tilted upward and that they do not touch the heat exchanger

- That the thermal overload protections of motors are well adjusted at the nominal intensity (three-phase motors only)

2- Check the power supply voltage to the terminals of the generator.

3- Select the ventilation mode and check the direction of rotation of the fans. Measure the intensity of each motor and compare it with the rating plate values.

4- Check that the type of gas and the inlet gas pressure are consistent with the appliance. Check that the main valve is well opened, purge the gas pipe. Switch on the valve located upstream to the generator

5– Check on the temperature controller that no sensor is at fault.

6- Put into service the generator

On the temperature controller, set the set temperature to a value higher than 3°C to the temperature of the premises, then, select the automatic mode.

Check that the burner works correctly and that the values of CO2 emissions are in accordance with the "technical Characteristics" table.  Read the instructions of burner.

Check visually that the flame of the burner is stable, and that it does not reach the bottom of the combustion chamber.

Vérifier que la température des gaz brulés est toujours supérieure au point de condensation (> 140°C), à la puissance de chauffage minimum.

7- Check that the FAN, LIMIT and LIMIT2 thermostats work correctly.

8- Effectuez une analyse de combustion selon les lois, les normes, les ordonnances etc. en vigueur

9- Draft a notebook of follow-up of the generator or the installation, in which you will annotate the compulsory notes according to the laws, the standards and the regulations in force.

Troubleshooting

Troubleshooting

In case of problem, always check that prerequisites in the smooth running of the generator ("Starting up" section) are performed.

If the control box is in safety mode («Voltage» indicator switched on, and «In operation» indicator switched off), reset.

WARNING

All electrical or mechanical interventions should be made when the power is turned off and the gas supply closed.

| Failure | Cause | Solution |
| --- | --- | --- |
| 1. The master switch (IG) is on -I- and the change-over switch in the –VENTILATION- position, but the indicator is off and the ventilation fan does not work. | The electrical board is not alive. The line fuse is burnt. | Check that the master switch upstream of the electrical board is on (-I-) Replace the fuse with another part, with the same characteristics |
| 2. As described in 1st section, but the “THERMAL OVERLOAD PROTECTION TRIPPING» indicator is lighted on | 1. The thermal overload protection has tripped by cutting the power supply of the motor. | 1. To re-engage, switch off the main switch (IG), open the lid of the electrical board and press on the button of the thermal overload protection - Check the breaker rating. |
| 3. The master switch is on -I-, the « POWER ON » indicator on, the over switch on –HEATING- the room thermostat on, but the burner does not work. | 1. Poor connection of the room thermostat and timer 2. Faulty burner 3. The LIMIT thermostat has tripped | 1. Call a technician for the replacement or the repair of the faulty part. 2. Call the after-sales service of the burner manufacturer. 3. Wait untill the air temperature has decreased to 65°C |
| 4. As described in 3rd section, but the « THERMOSTAT LIMIT2 THERMOSTAT TRIPPING » indicator lighted on. | 1. The LIMIT2 thermostat has tripped because of overheated air (over 100°C). Lower air flow rate due to a pressure drop in the inlet or outlet air circuit. Blocked filters (if any) Stop of the generator by the master switch or lack of current while running. Tripping of the fire valve. Bulbs-sensors of the Thermostat are tilted downward or too near of the heat exchanger, which radiation causes their too early tripping. | 1. Do, as described in the « TRITHERMOSTAT» section to reset the burner. |
| 5. As described in 3rd section, but the burner has stopped after the pre-sweeping stage and no flame has occurred. | 1. Faulty burner or lack of gas. | 1. Call the after-sales service of the burner manufacturer. |
| 6. The burner works, but the ventilation fan is delayed before running and once started, then, starts/stops continuously. | 1. Too high setting of the FAN Thermostat. 2. FAN thermostat. 3. The temperature of the recycling air is below 0°C. 4. Too low gas flow rate. | 1. Set it at 35°C (See “TRITHERMOSTAT” section) 2. Call a technician to replace it. 3. Try to increase this temperature. 4. Call the after-sales service of the burner manufacturer. |
| 7. The burner works but the ventilation fan does not start and the « THERMOSTAT LIMIT2 THERMOSTAT TRIPPING » indicator lighted on. | The motor has tripped the thermal overheated protection. Faulty electric motor(s), defective contacts or seized bearings. | Re-engage, as described in the section 2. Call the after-sales service of the burner manufacturer. |
| 8. During the operation, the burner has stopped without control of the timer or the thermostat. | The LIMIT thermostat has tripped. The safety LIMIT2 thermostat has tripped. Lower air flow rate due to a pressure drop in the inlet or outlet air circuit. Blocked filters (if any) Stop of the generator by the master switch or lack of current while running. Tripping of the fire valve. Bulbs-sensors of the Thermostat are tilted downward or too near of the heat exchanger, which radiation causes their too early tripping. | 1. Do, as described in the « TRITHERMOSTAT » section to reset the burner. |

REMARK: FOR THE BREAKDOWNS OF THE BURNER, READ THE TECHNICAL INSTRUCTIONS OF THE BURNER

WARNING

Warning, only genuine manufacturer parts ensure product and people safety. The use of parts other than genuine ones invokes the responsibility of the individual and will void the product warranty.

Record in follow-up notebook of the device or the installation all the replacements of parts.

Spare parts

Exploded view

| Nº | Designation | Nº | Designation |
| --- | --- | --- | --- |
| 2 | Fan | 18 | Thermostat |
| 3 | Motor | 20 | Joint of the mounting plate |
| 4 | Pulley – fan side | 21 | Mounting plate of the burner |
| 5 | Pulley – motor side | 22 | Joint of the combustion chamber |
| 6 | Belt | 24 | Light indicator |
| 7 | Electrical board | 25 | Joint of the smoke box |
|  |  | 26 | Turbulator |

WARNING

Do contact SOLARONICS CHAUFFAGE before replacing any other parts.

Maintenance

A proper and regular maintenance, at least once a year, determine an efficient and effective functioning, a minimum consumption and an important longevity.

WARNING

The gas device must be maintained cold and with electric power cut

These works can be performed by a qualified technician only

| Parts | Maintenance operations |
| --- | --- |
| Air outlet and recycling grids | Nettoyage à la brosse et/ou à l’aspirateur |
| Filters | The filter is an accessory. A blocked filter reduces the air flow, thus increases the outlet air temperature and reduces the exchange of heat and the efficiency of the generator. It is thus very important to clean regularly the filter to maintain it clean. The frequency of the cleaning depends on the quantity of dust being in the filtered air. For the cleaning, operate as follows: - Remove the filter of its frame - Shake it and drop the dust - Blow the filter with some compressed air against the current - Regularly, for a better well-kept cleaning, wash the filter in tepid water with a detergent, dry it and put it back in place. CAUTION! After three washes, the filter must be replaced by a new one having the same code. |
| Burner | For the burner maintenance, comply with the technical instructions of the burner. En outre, vérifiez l’étanchéité de l’alimentation en combustible. Vérifiez également l’étanchéité de la buse de fumées. |
| Chimneys | Check air combustion ducts and flue gas ducts. Pipes must be tight in smokes and corrosion-resistant. They must be annually checked. |
| Combustion analysis | At least once, at the beginning of every season of heating, and more often if the regulations require it, make an analysis of combustion and record the results in the follow-up notebook of the device or the installation. Check the pressure of gas supply and analyze the combustion of the device. During the control, check that the probe of analysis is tight at the level of the point of taking, the extremity of the probe set in the center of the exhaust duct of smokes. |
| Groupe de ventilation | At least once, at the beginning of every season, check: - The correct alignment of pulleys and drive belts (if any), as well as the wear of belts (if need be, replace them by belts of the same size) - The direction of rotation of ventilation fan, indicated by the arrow on the fan (see picture 6) - The tension of belts: by tightening them in hands, their flexion has to be about 2-3 cm (see picture 13). To adjust the tension, screw or undo the stretching screw of the belt located on the engine slider (18). - The absorbed current of the motor(s) shall not exceed the rating plaque values. - The correct operating of the thermostats set of the generator. Fig.6 |
| Heat exchanger | Soot and scoria shall be removed from the heat exchanger so as to keep its efficiency. The cleaning must be made at the end of every season of heating, or more often if the heat exchanger requires it. If the burner does not start easily, the cause can be the soot accumulating in the heat exchanger and blocking the passage of combustion gases. Formation of soot can depend on various causes, such as: a bad draft, a burner with a low air supply. To clean the heat exchanger, operate as follows: Pipes of the heat exchanger (10) Remove the cover of the smoke box (2). Remove the turbulators and clean tubes inside. Remove the soot at the front side so as to avoid it to fall in the combustion chamber. Before reinstalling the cover of the smoke box, check that its joints are intact; otherwise replace them by joints having the same code. Remove the pipe on the joint of the chimney (8) and clean the back smoke box (9). Combustion chamber (11) Remove the burner of its mounting plate (4). Remove the soot and the scoria from the internal walls. Check that the combustion chamber did not undergo damage. Check that the joint of the mounting plate of the burner as well as the internal corresponding inside one, on the grid are in good condition, otherwise replace them by joints having the same code Remarque : Aucun joint ne comporte d’amiante, en conformité avec les normes de la CEE. L’humidité de la suie signifie que les gaz brûlés se condensent et entraînent la corrosion de l’échangeur de chaleur ; évitez donc cette défaillance. Pour cela, la température des gaz brulés doit être toujours supérieure au point de condensation (> 140 °C). |

- Warranty

Your appliance has a contractual guaranty against any manufacturing defect.

Solaronics Chauffage is not responsible for improper use of the device, failure or insufficient maintenance, or improper installation of the appliance (it is your responsibility to ensure that it is carried out by a qualified professional).

In particular, Solaronics Chauffage will not be liable for any damage, loss or injury caused by improper installation that does not comply:

•	with rules in force or imposed by the local authorities

•	with national, or even local and specific rules governing the installation

•	with our technical instructions, in particular, for maintenance of the devices

•	with the good engineering pratice

Solaronics Chauffage warranty is limited to replacement or repair of defective parts only by our services excluding labor costs, travel and transport.

Our warranty does not cover replacement or repair of damaged parts by normal wear and tear, misuse, unskilled third party interventions, defect or failure in monitoring or maintenance, non-compliant power supply or use of an inappropriate fuel or of poor quality.

Subsets, such as motors, pumps, electric valves, etc ... are only guaranteed if they have never been removed.

Rights established by the European Directive 1999/44/CEE remain valid.

APPENDIX

END OF LIFE OF EQUIPMENT

This device contains electrical and / or electronic components and should not be considered as household waste. Ensure compliance with applicable standards and regulations for waste disposal when dismantling.

THE RIGHT THING FOR THE SAFETY

- Keep ventilation in good condition:

- Keep free and clear air inlets and outlets (grids, vents ...)

- Check annually flues ducts.

-  Maintain equipment:

Maintain or make maintain the equipment by a competent person at appropriate intervals, following the manufacturer's recommendations

- Check the gas appliance by a competent person in case of triggering of a safety device

SMELL GAS? GOOD REACTIONS

Flammable but non toxic, gas has been odorized to allow discovering any leak, even small.

This smell allows you to react fast. If you smell gas, close the gas valve and check the equipment. If everything is normal and the smell persists, you have to have the good reflexes

DO NOT PROVOKE ANY FLAME OR SPARK … AND DO NOT USE ELECTRICAL APPLIANCES.

- Do not call an elevator, use a phone, even mobile, press an electric switch, not to create a spark.

Whatever the room where the gas smell is perceived, ventilate this room as much as possible by opening windows and doors.

“Gas troubleshooting" service is at your disposal 24/24 and 7/7 at the gas distributor. This service reacts free of charge and as soon as possible in case of gas leak or smell.

- The phone number is: ……………………………, it is noted on the invoices

The number of the emergency services (fire) is: …………………………...

PA Villa Parc – Immeuble « le chêne »

12 allée Lech Walesa

77185 Lognes – FRANCE

Agence Service

Ile-de-France

Siège

ZI n°3, 78 rue du Kemmel – CS 20302

59429 ARMENTIÈRES Cedex

Tél. : +33(0) 3 20 10 59 59

Fax : +33(0) 3 20 35 57 22

Catalogue Pièces de Rechange

Disponible sur simple demande